## Disclaimer
© 2011 ASHRAE
DISCLAIMER
By using this spreadsheet, the user acknowledges and agrees to the following terms:
The resources supplied here are for personal and office use by purchasers of Procedures for Commercial Building Energy Audits, Second Edition. These resources are provided “as is” without warranty of any kind, either expressed or implied. The entire risk as to the quality and performance of the resources is with the user. In no event will ASHRAE be liable to the user for any damages, including without limitation any lost profits, lost savings, or other incidental or consequential damages arising out of the use of or inability to use these resources.

## Checklist
Procedures for Commercial Building Energy Audits, Second Edition
Hourly Simulation Checklist
Input Verification
Project
Verify correct weather file/zone
Specify correct site altitude
Specify ground reflectance (account for major factors such as nearby lake or mountain ridge)
Specify correct utility rate schedules
Envelope
Specify walls, windows, floors, and underground floor constructions per drawings
Verify constructions per drawings (especially if "wizard" inputs are used)
Specify window and frame properties (and check correct treatment of outdoor air coefficient)
Verify slab heat transfer coefficients as appropriate
Verify building floor area (omit plenums)
Include skylights if needed—make sure they are not obscured by roof constructions
Include window overhangs where needed
Include exterior shading from other parts of building
Include exterior shading from other buildings
Spaces
Verify equipment internal load density (W/ft^2, W/m^2)
Verify equipment schedules
Verify lighting loads density (W/ft^2, W/m^2)
Verify lighting schedules
Verify occupancy loads (number of people or area per person)
Verify occupancy schedules
Verify infiltration loads (air changes per hour or flow per unit area)
Verify infiltration schedules
Add daylighting controls as appropriate
Zones
Verify zones are consistent with building construction (conditioned, unconditioned, plenums, etc.)
Verify zone thermostat setpoints and schedules
Set outdoor airflow/person in zones
Air-Side Systems
Assign zones to correct systems and specify control zone as appropriate
Verify equipment operating schedules
Size systems
Size heating coil capacities (auto-sizing is discouraged)
Size cooling coil capacities (auto-sizing is discouraged)
Add exhaust fans and controls as needed
Ensure fan energy and compressor power are separate (packaged units)
Verify supply air setpoints and resets
Plants
Specify configuration of hot-water, condenser-water, and chilled-water loops
(You may need separate loops for primary and secondary loops)
Verify equipment operating schedules, capacities, and part-load efficiencies
Boiler(s) (if multiple, ensure correct staging)
Chiller(s) (if multiple, ensure correct staging)
Pump(s) (if multiple, ensure correct staging)
Verify equipment control sequences
Check pump definitions use (1) kW input or (2) flow rate, pressure drop, and efficiency (not both)
Output Verification
Review building performance summary reports
Check overall EUI (compare with known benchmarks)
Check consistency with historical utility billing data (all end uses)
Check end-use splits for reasonableness (compare with known benchmarks)
Check end-use splits for reasonableness (compare with known benchmarks or sub-metered data)
Equipment/plug loads
Lighting
Final occupant density
Check final equipment design/sizing
Cooling capacity
Heating capacity
Airflow
Loop sizing, flow rates
Ventilation design flow rate
Check final system summary performance
Heating average system efficiency
Cooling average system efficiency
Review detailed hourly reports and check loads are met (zones and plant)
Check loads are met (zones and plant)
Verify hourly equipment schedules
© 2011 ASHRAE
Use this checklist as a guide to ensure that your model is reasonable and accurate. Note that completing every item on this list will not guarantee that your model is accurate and represents your building. Use engineering judgment to investigate any items that seem aberrant and pay special attention to unusual systems and components in your building.
Note on J17: Jim Kelsey: In some programs, you must subtract out the contribution from the outside air film coefficient